## Steam TracerTables
Steam Tracer Sizing Tables
Notes:
1. Steam Tracing should be carefully evaluated based on freezing potential of pipe fluid
2. For steam pressure to 12 barg and line temperatures to 204°C, ASTM B-88 Type 'K' copper water tubing should be used.
3. For steam pressures above 12 barg and line temperatures to 204°C, SS tubing or Schedule 80 CS pipe tracers can be used.
4. SS tubing should be used if heat transfer cement is required. SS tubing should also be used in applications such as tracing
instrument leads and where a great deal of bending is required such as valve manifolds or pump casings.
5. Schedule 80 CS pipe tracers should be used where the tracer is welded the pipe. Its joints, under insulation should be welded.
6. The tabular guide for stream tracing is not recommended for tracing of glycol and hot oil systems
7. For deriving tubing OD based on nominal diameter given in tables, add 1/8 inch to the nominal diameter
8. Low Pressure steam (1 barg or 15 psig) should not be used where ambient temperatures can reach below freezing point of water.
-17.8°C Ambient Temperature - 2.76 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
1.5 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
2 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
3 | 1 | 3/8 | 9 | 1 | 3/8 | 9
4 | 1 | 3/8 | 9 | 1 | 3/8 | 9
6 | 1 | 3/8 | 10.4 | 1 | 5/8 | 13.4
8 | 1 | 3/8 | 10.4 | 1 | 5/8 | 13.4
10 | 1 | 3/8 | 11.9 | 1 | 5/8 | 14.8
12 | 1 | 3/8 | 11.9 | 1 | 1 | 17.8
14 | 1 | 3/8 | 13.4 | 1 | 1 | 19.3
16 | 1 | 3/8 | 13.4 | 1 | 1 | 20.8
18 | 1 | 3/8 | 13.4 | 2 | 5/8 | 25.3
20 | 1 | 3/8 | 13.4 | 2 | 5/8 | 26.8
24 | 1 | 5/8 | 17.8 | 2 | 5/8 | 28.3
Stm Rate: kg/h per 100 m
-17.8°C Ambient Temperature - 2.76 barg steam
Sch 80 Pipe tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
1.5 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
2 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
3 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
4 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
6 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
8 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
10 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
12 | 1 | 1/2 | 14.8 | 1 | 3/4 | 17.8
14 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
16 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
18 | 1 | 1/2 | 17.8 | 2 | 1 | 23.8
20 | 1 | 1/2 | 17.8 | 2 | 1/2 | 28.3
24 | 1 | 1/2 | 19.3 | 2 | 1/2 | 30
Stm Rate: kg/h per 100 m
-17.8°C Ambient Temperature - 2.76 barg steam
Copper Tubing tracers with cement
Process Line Size | Maintained Temperature
| 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1
1.5
2
3
4
6
8
10
12
14
16
18 | 1 | 3/8 | 32.7
20 | 1 | 3/8 | 34.2
24 | 1 | 3/8 | 37.2
Stm Rate: kg/h per 100 m
-17.8°C Ambient Temperature - 10 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
1.5 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
2 | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 5/8 | 13.4
3 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 1 | 17.8
4 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 1 | 19.3
6 | 1 | 3/8 | 14.8 | 1 | 3/8 | 14.8 | 1 | 5/8 | 19.3 | 1 | 1 | 20.8
8 | 1 | 3/8 | 16.4 | 1 | 3/8 | 16.4 | 1 | 5/8 | 20.8 | 2 | 5/8 | 26.8
10 | 1 | 3/8 | 17.8 | 1 | 3/8 | 17.8 | 1 | 1 | 25.3 | 2 | 5/8 | 29.8
12 | 1 | 3/8 | 19.3 | 1 | 3/8 | 19.3 | 1 | 1 | 28.3 | 2 | 1 | 37.2
14 | 1 | 3/8 | 19.3 | 1 | 5/8 | 20.8 | 1 | 1 | 29.8 | 2 | 1 | 40.2
16 | 1 | 3/8 | 20.8 | 1 | 5/8 | 25.3 | 2 | 5/8 | 37.2 | 2 | 1 | 43.1
18 | 1 | 3/8 | 20.8 | 2 | 5/8 | 26.8 | 2 | 5/8 | 38.7 | 3 | 1 | 52.1
20 | 1 | 3/8 | 20.8 | 2 | 5/8 | 26.8 | 2 | 5/8 | 40.2 | 3 | 1 | 55
24 | 1 | 3/8 | 22.3 | 2 | 1 | 35.7 | 2 | 1 | 52.1 | 3 | 1 | 61
Stm Rate: kg/h per 100 m
-17.8°C Ambient Temperature - 10 barg steam
Sch 80 Pipe tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
1.5 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
2 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
3 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 3/4 | 17.8
4 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
6 | 1 | 1/2 | 19.3 | 1 | 1/2 | 19.3 | 1 | 3/4 | 19.3 | 1 | 3/4 | 20.8
8 | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 1 | 1 | 25.3
10 | 1 | 1/2 | 22.3 | 1 | 1/2 | 22.3 | 1 | 3/4 | 25.3 | 2 | 1/2 | 29.8
12 | 1 | 1/2 | 23.8 | 1 | 1/2 | 23.8 | 1 | 3/4 | 26.8 | 2 | 3/4 | 35.7
14 | 1 | 1/2 | 25.3 | 1 | 1/2 | 25.3 | 1 | 3/4 | 28.3 | 2 | 3/4 | 38.7
16 | 1 | 1/2 | 25.3 | 1 | 1/2 | 25.3 | 1 | 1 | 34.2 | 2 | 3/4 | 41.7
18 | 1 | 1/2 | 26.8 | 1 | 1/2 | 26.8 | 2 | 1/2 | 38.7 | 2 | 1 | 47.6
20 | 1 | 1/2 | 28.3 | 1 | 1/2 | 28.3 | 2 | 1/2 | 40.2 | 3 | 3/4 | 53.6
24 | 1 | 1/2 | 28.3 | 1 | 3/4 | 34.2 | 2 | 3/4 | 41.7 | 3 | 3/4 | 59.5
Stm Rate: kg/h per 100 m
-17.8°C Ambient Temperature - 10 barg steam
Copper Tubing tracers with cement
Process Line Size | Maintained Temperature
| 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1
1.5
2
3
4
6
8 | [6 empty] | 1 | 3/8 | 28.3
10 | [6 empty] | 1 | 3/8 | 31.2
12 | [6 empty] | 1 | 3/8 | 34.2
14 | [6 empty] | 1 | 3/8 | 37.2
16 |  |  |  | 1 | 3/8 | 40.2 | 1 | 3/8 | 40.2
18 |  |  |  | 1 | 3/8 | 43.1 | 1 | 5/8 | 50.6
20 |  |  |  | 1 | 3/8 | 46.1 | 1 | 5/8 | 53.6
24 |  |  |  | 1 | 3/8 | 50.6 | 1 | 5/8 | 59.5
Stm Rate: kg/h per 100 m
-7°C Ambient Temperature - 2.76 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
1.5 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
2 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
3 | 1 | 3/8 | 7.4 | 1 | 3/8 | 7.4
4 | 1 | 3/8 | 9 | 1 | 3/8 | 9
6 | 1 | 3/8 | 9 | 1 | 3/8 | 9
8 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
10 | 1 | 3/8 | 10.4 | 1 | 5/8 | 13.4
12 | 1 | 3/8 | 11.9 | 1 | 5/8 | 13.4
14 | 1 | 3/8 | 11.9 | 1 | 5/8 | 14.8
16 | 1 | 3/8 | 11.9 | 1 | 1 | 17.8
18 | 1 | 3/8 | 11.9 | 1 | 1 | 19.3
20 | 1 | 3/8 | 13.4 | 1 | 1 | 20.8
24 | 1 | 3/8 | 13.4 | 2 | 5/8 | 26.8
Stm Rate: kg/h per 100 m
-7°C Ambient Temperature - 2.76 barg steam
Sch 80 Pipe tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
1.5 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
2 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
3 | 1 | 1/2 | 10.4 | 1 | 1/2 | 10.4
4 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
6 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
8 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
10 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
12 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
14 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
16 | 1 | 1/2 | 14.8 | 1 | 3/4 | 17.8
18 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
20 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
24 | 1 | 1/2 | 17.8 | 1 | 1 | 23.8
Stm Rate: kg/h per 100 m
-7°C Ambient Temperature - 2.76 barg steam
Copper Tubing tracers with cement
Process Line Size | Maintained Temperature
| 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1
1.5
2
3
4
6
8
10
12
14
16
18
20
24 | 1 | 3/8 | 34.2
Stm Rate: kg/h per 100 m
-7°C Ambient Temperature - 10 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
1.5 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
2 | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 5/8 | 13.4
3 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 5/8 | 14.8
4 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 1 | 19.3
6 | 1 | 3/8 | 14.8 | 1 | 3/8 | 14.8 | 1 | 3/8 | 14.8 | 1 | 1 | 20.8
8 | 1 | 3/8 | 16.4 | 1 | 3/8 | 16.4 | 1 | 5/8 | 19.3 | 2 | 5/8 | 25.3
10 | 1 | 3/8 | 16.4 | 1 | 3/8 | 16.4 | 1 | 5/8 | 20.8 | 2 | 5/8 | 28.3
12 | 1 | 3/8 | 17.8 | 1 | 3/8 | 17.8 | 1 | 1 | 26.8 | 2 | 5/8 | 29.8
14 | 1 | 3/8 | 17.8 | 1 | 3/8 | 17.8 | 1 | 1 | 28.3 | 2 | 1 | 37.2
16 | 1 | 3/8 | 19.3 | 1 | 3/8 | 19.3 | 1 | 1 | 29.8 | 2 | 1 | 40.2
18 | 1 | 3/8 | 19.3 | 1 | 3/8 | 19.3 | 2 | 5/8 | 37.2 | 2 | 1 | 43.1
20 | 1 | 3/8 | 19.3 | 1 | 5/8 | 25.3 | 2 | 5/8 | 38.7 | 3 | 1 | 55
24 | 1 | 3/8 | 20.8 | 1 | 5/8 | 26.8 | 2 | 5/8 | 41.7 | 3 | 1 | 59.5
Stm Rate: kg/h per 100 m
-7°C Ambient Temperature - 10 barg steam
Sch 80 Pipe tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
1.5 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
2 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
3 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
4 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 3/4 | 17.8
6 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
8 | 1 | 1/2 | 19.3 | 1 | 1/2 | 19.3 | 1 | 1/2 | 19.3 | 1 | 1 | 23.8
10 | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 2 | 1/2 | 29.8
12 | 1 | 1/2 | 22.3 | 1 | 1/2 | 22.3 | 1 | 3/4 | 25.3 | 2 | 1/2 | 31.2
14 | 1 | 1/2 | 23.8 | 1 | 1/2 | 23.8 | 1 | 3/4 | 26.8 | 2 | 3/4 | 35.7
16 | 1 | 1/2 | 23.8 | 1 | 1/2 | 23.8 | 1 | 3/4 | 28.3 | 2 | 3/4 | 40.2
18 | 1 | 1/2 | 25.3 | 1 | 1/2 | 25.3 | 1 | 1 | 32.7 | 2 | 3/4 | 43.1
20 | 1 | 1/2 | 25.3 | 1 | 1/2 | 25.3 | 2 | 1/2 | 40.2 | 2 | 1 | 47.6
24 | 1 | 1/2 | 26.8 | 1 | 1/2 | 26.8 | 2 | 1/2 | 43.1 | 3 | 3/4 | 56.5
Stm Rate: kg/h per 100 m
-7°C Ambient Temperature - 10 barg steam
Copper Tubing tracers with cement
Process Line Size | Maintained Temperature
| 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1
1.5
2
3
4 | [12 empty] | `
6
8 | [6 empty] | 1 | 3/8 | 26.8
10 | [6 empty] | 1 | 3/8 | 29.8
12 | [6 empty] | 1 | 3/8 | 32.7
14 | [6 empty] | 1 | 3/8 | 35.7
16 | [6 empty] | 1 | 3/8 | 38.7
18 |  |  |  | 1 | 3/8 | 41.7 | 1 | 3/8 | 41.7
20 |  |  |  | 1 | 3/8 | 43.1 | 1 | 5/8 | 50.6
24 |  |  |  | 1 | 3/8 | 47.6 | 1 | 5/8 | 56.5
Stm Rate: kg/h per 100 m
4°C Ambient Temperature - 2.76 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 3/8 | 6
1.5 |  |  |  | 1 | 3/8 | 6
2 |  |  |  | 1 | 3/8 | 7.4
3 |  |  |  | 1 | 3/8 | 7.4
4 |  |  |  | 1 | 3/8 | 7.4
6 |  |  |  | 1 | 3/8 | 9
8 |  |  |  | 1 | 3/8 | 9
10 |  |  |  | 1 | 3/8 | 10.4
12 |  |  |  | 1 | 3/8 | 10.4
14 |  |  |  | 1 | 5/8 | 11.9
16 |  |  |  | 1 | 5/8 | 13.4
18 |  |  |  | 1 | 5/8 | 14.8
20 |  |  |  | 1 | 1 | 17.8
24 |  |  |  | 1 | 1 | 19.3
Stm Rate: kg/h per 100 m
4°C Ambient Temperature - 2.76 barg steam
Sch 80 Pipe Tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 1/2 | 9
1.5 |  |  |  | 1 | 1/2 | 10.4
2 |  |  |  | 1 | 1/2 | 10.4
3 |  |  |  | 1 | 1/2 | 10.4
4 |  |  |  | 1 | 1/2 | 10.4
6 |  |  |  | 1 | 1/2 | 11.9
8 |  |  |  | 1 | 1/2 | 11.9
10 |  |  |  | 1 | 1/2 | 13.4
12 |  |  |  | 1 | 1/2 | 13.4
14 |  |  |  | 1 | 1/2 | 13.4
16 |  |  |  | 1 | 1/2 | 14.8
18 |  |  |  | 1 | 3/4 | 14.8
20 |  |  |  | 1 | 3/4 | 17.8
24 |  |  |  | 1 | 3/4 | 19.3
Stm Rate: kg/h per 100 m
4°C Ambient Temperature - 10 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 3/8 | 9 | 1 | 3/8 | 9 | 1 | 3/8 | 9
1.5 |  |  |  | 1 | 3/8 | 9 | 1 | 3/8 | 9 | 1 | 3/8 | 9
2 |  |  |  | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
3 |  |  |  | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 5/8 | 13.4
4 |  |  |  | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 5/8 | 14.8
6 |  |  |  | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 1 | 19.3
8 |  |  |  | 1 | 3/8 | 14.8 | 1 | 3/8 | 14.8 | 1 | 1 | 20.8
10 |  |  |  | 1 | 3/8 | 16.4 | 1 | 5/8 | 19.3 | 2 | 5/8 | 25.3
12 |  |  |  | 1 | 3/8 | 16.4 | 1 | 5/8 | 20.8 | 2 | 5/8 | 28.3
14 |  |  |  | 1 | 3/8 | 17.8 | 1 | 1 | 26.8 | 2 | 5/8 | 31.2
16 |  |  |  | 1 | 3/8 | 17.8 | 1 | 1 | 28.3 | 2 | 1 | 37.2
18 |  |  |  | 1 | 3/8 | 17.8 | 1 | 1 | 28.3 | 2 | 1 | 40.2
20 |  |  |  | 1 | 3/8 | 19.3 | 1 | 1 | 29.8 | 2 | 1 | 41.7
24 |  |  |  | 1 | 3/8 | 19.3 | 2 | 5/8 | 38.7 | 3 | 1 | 53.5
Stm Rate: kg/h per 100 m
4°C Ambient Temperature - 10 barg steam
Sch 80 Pipe Tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
1.5 |  |  |  | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
2 |  |  |  | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
3 |  |  |  | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
4 |  |  |  | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
6 |  |  |  | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 3/4 | 19.3
8 |  |  |  | 1 | 1/2 | 17.8 | 1 | 1/2 | 17.8 | 1 | 3/4 | 20.8
10 |  |  |  | 1 | 1/2 | 19.3 | 1 | 1/2 | 19.3 | 1 | 1 | 23.8
12 |  |  |  | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 2 | 1/2 | 29.8
14 |  |  |  | 1 | 1/2 | 22.3 | 1 | 3/4 | 25.3 | 2 | 1/2 | 32.7
16 |  |  |  | 1 | 1/2 | 22.3 | 1 | 3/4 | 26.8 | 2 | 3/4 | 35.7
18 |  |  |  | 1 | 1/2 | 23.8 | 1 | 3/4 | 26.8 | 2 | 3/4 | 38.7
20 |  |  |  | 1 | 1/2 | 23.8 | 1 | 3/4 | 28.3 | 2 | 3/4 | 41.7
24 |  |  |  | 1 | 1/2 | 25.3 | 1 | 1 | 35.7 | 2 | 1 | 50.6
Stm Rate: kg/h per 100 m
4°C Ambient Temperature - 10 barg steam
Copper Tubing tracers with cement
Process Line Size | Maintained Temperature
| 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1
1.5
2
3
4
6
8
10 | [6 empty] | 1 | 3/8 | 26.8
12 | [6 empty] | 1 | 3/8 | 29.8
14 | [6 empty] | 1 | 3/8 | 32.7
16 | [6 empty] | 1 | 3/8 | 35.7
18 | [6 empty] | 1 | 3/8 | 38.7
20 | [6 empty] | 1 | 5/8 | 40.2
24 |  |  |  | 1 | 3/8 | 44.6 | 1 | 5/8 | 53.6
Stm Rate: kg/h per 100 m
15.6°C Ambient Temperature - 2.76 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 3/8 | 6
1.5 |  |  |  | 1 | 3/8 | 6
2 |  |  |  | 1 | 3/8 | 6
3 |  |  |  | 1 | 3/8 | 7.4
4 |  |  |  | 1 | 3/8 | 7.4
6 |  |  |  | 1 | 3/8 | 7.4
8 |  |  |  | 1 | 3/8 | 9
10 |  |  |  | 1 | 3/8 | 9
12 |  |  |  | 1 | 3/8 | 9
14 |  |  |  | 1 | 3/8 | 10.4
16 |  |  |  | 1 | 3/8 | 10.4
18 |  |  |  | 1 | 3/8 | 10.4
20 |  |  |  | 1 | 3/8 | 10.4
24 |  |  |  | 1 | 5/8 | 14.8
Stm Rate: kg/h per 100 m
15.6°C Ambient Temperature - 2.76 barg steam
Sch 80 Pipe Tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 1/2 | 9
1.5 |  |  |  | 1 | 1/2 | 10.4
2 |  |  |  | 1 | 1/2 | 10.4
3 |  |  |  | 1 | 1/2 | 10.4
4 |  |  |  | 1 | 1/2 | 10.4
6 |  |  |  | 1 | 1/2 | 11.9
8 |  |  |  | 1 | 1/2 | 11.9
10 |  |  |  | 1 | 1/2 | 13.4
12 |  |  |  | 1 | 1/2 | 13.4
14 |  |  |  | 1 | 1/2 | 13.4
16 |  |  |  | 1 | 1/2 | 14.8
18 |  |  |  | 1 | 1/2 | 14.8
20 |  |  |  | 1 | 1/2 | 14.8
24 |  |  |  | 1 | 1/2 | 14.8
Stm Rate: kg/h per 100 m
15.6°C Ambient Temperature - 10 barg steam
Copper tubing tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 3/8 | 9 | 1 | 3/8 | 9 | 1 | 3/8 | 9
1.5 |  |  |  | 1 | 3/8 | 9 | 1 | 3/8 | 9 | 1 | 3/8 | 9
2 |  |  |  | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4
3 |  |  |  | 1 | 3/8 | 10.4 | 1 | 3/8 | 10.4 | 1 | 5/8 | 11.9
4 |  |  |  | 1 | 3/8 | 11.9 | 1 | 3/8 | 11.9 | 1 | 5/8 | 13.4
6 |  |  |  | 1 | 3/8 | 13.4 | 1 | 3/8 | 13.4 | 1 | 5/8 | 14.8
8 |  |  |  | 1 | 3/8 | 13,4 | 1 | 3/8 | 13.4 | 1 | 1 | 19.3
10 |  |  |  | 1 | 3/8 | 14.8 | 1 | 3/8 | 14.8 | 2 | 1 | 20.8
12 |  |  |  | 1 | 3/8 | 14.8 | 1 | 5/8 | 19.3 | 2 | 5/8 | 26.8
14 |  |  |  | 1 | 3/8 | 16.4 | 1 | 5/8 | 20.8 | 2 | 5/8 | 28.3
16 |  |  |  | 1 | 3/8 | 16.4 | 1 | 5/8 | 20.8 | 2 | 5/8 | 31.2
18 |  |  |  | 1 | 3/8 | 17.8 | 1 | 1 | 26.8 | 2 | 1 | 37.2
20 |  |  |  | 1 | 3/8 | 17.8 | 1 | 1 | 28.3 | 2 | 1 | 40.2
24 |  |  |  | 1 | 3/8 | 17.8 | 1 | 1 | 29.8 | 3 | 1 | 43.1
Stm Rate: kg/h per 100 m
15.6°C Ambient Temperature - 10 barg steam
Sch 80 Pipe Tracers without cement
Process Line Size | Maintained Temperature
| 10°C |  |  | 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1 |  |  |  | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9 | 1 | 1/2 | 11.9
1.5 |  |  |  | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
2 |  |  |  | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
3 |  |  |  | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4 | 1 | 1/2 | 13.4
4 |  |  |  | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8 | 1 | 1/2 | 14.8
6 |  |  |  | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4 | 1 | 1/2 | 16.4
8 |  |  |  | 1 | 1/2 | 17.8 | 1 | 1/2 | 17.8 | 1 | 3/4 | 19.3
10 |  |  |  | 1 | 1/2 | 17.8 | 1 | 1/2 | 17.8 | 1 | 3/4 | 20.8
12 |  |  |  | 1 | 1/2 | 19.3 | 1 | 1/2 | 19.3 | 1 | 1 | 25.3
14 |  |  |  | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 2 | 1/2 | 26.8
16 |  |  |  | 1 | 1/2 | 20.8 | 1 | 1/2 | 20.8 | 2 | 1/2 | 29.8
18 |  |  |  | 1 | 1/2 | 22.3 | 1 | 3/4 | 26.8 | 2 | 3/4 | 35.7
20 |  |  |  | 1 | 1/2 | 22.3 | 1 | 3/4 | 26.8 | 2 | 3/4 | 38.7
24 |  |  |  | 1 | 1/2 | 23.8 | 1 | 3/4 | 28.3 | 2 | 3/4 | 43.1
Stm Rate: kg/h per 100 m
15.6°C Ambient Temperature - 10 barg steam
Copper Tubing tracers with cement
Process Line Size | Maintained Temperature
| 38°C |  |  | 66°C |  |  | 93°C
| Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate | Tracer Qty | Nom. Dia | Stm Rate
1
1.5
2
3
4
6
8
10
12 | [6 empty] | 1 | 3/8 | 26.8
14 | [6 empty] | 1 | 3/8 | 29.8
16 | [6 empty] | 1 | 3/8 | 32.7
18 | [6 empty] | 1 | 3/8 | 35.7
20 | [6 empty] | 1 | 3/8 | 38.7
24 | [6 empty] | 1 | 3/8 | 41.7
Stm Rate: kg/h per 100 m
Prepared by: |  | Ankur Srivastava
Chemical Engineer
Email: | ankur_2061@hotmail.com

## Max Stm Tracer Length for traps
The tables below are based on a pressure drop of 10% of the inlet pressure in barg or
0.7 bar, whichever is greater, with maximum length not to exceed 152 m (500 ft)
Maximum Steam Tracer Length between Traps - 3/8 inch Nominal (1/2 inch OD) tube (Copper or SS)
Length of tracers, m
kg/h steam per 100 m tracer tube | 1 barg steam | 2.76 barg steam | 10 barg steam
7.4 | 61 | 94 | 152
14.8 | 37 | 61 | 125
22.3 | 30.5 | 46 | 97
30 | 24 | 40 | 79
37 | - | 33 | 67
45 | - | 30.5 | 61
52 | - | - | 55
60 | - | - | 49
Maximum Steam Tracer Length between Traps - 5/8 inch Nominal (3/4 inch OD) tube (Copper or SS)
Length of tracers, m
kg/h steam per 100 m tracer tube | 1 barg steam | 2.76 barg steam | 10 barg steam
7.4 | 137 | 152 | 152
14.8 | 97 | 149 | 152
22.3 | 73 | 116 | 152
30 | 61 | 94 | 152
37 | 55 | 85 | 152
45 | 49 | 76 | 152
52 | 43 | 67 | 137
60 | 40 | 61 | 125
67 | 37 | 55 | 116
Maximum Steam Tracer Length between Traps - 1 inch Nominal (1 1/8 inch OD) tube (Copper or SS)
Length of tracers, m
kg/h steam per 100 m tracer tube | 1 barg steam | 2.76 barg steam | 10 barg steam
7.4 | 152 | 152 | 152
14.8 | 152 | 152 | 152
22.3 | 152 | 152 | 152
30 | 152 | 152 | 152
37 | 152 | 152 | 152
45 | 137 | 152 | 152
52 | 125 | 152 | 152
60 | 110 | 152 | 152
67 | 91 | 152 | 152
Maximum Steam Tracer Length between Traps - 1 /2 inch Sch 80 pipe (CS pipe)
Length of tracers, m
kg/h steam per 100 m tracer pipe | 1 barg steam | 2.76 barg steam | 10 barg steam
7.4 | 82 | 128 | 152
14.8 | 52 | 82 | 152
22.3 | 40 | 61 | 134
30 | 33 | 55 | 107
37 | - | 46 | 91
45 | - | 40 | 82
Maximum Steam Tracer Length between Traps - 3 /4 inch Sch 80 pipe (CS pipe)
Length of tracers, m
kg/h steam per 100 m tracer pipe | 1 barg steam | 2.76 barg steam | 10 barg steam
7.4 | 140 | 152 | 152
14.8 | 97 | 149 | 152
22.3 | 73 | 116 | 152
30 | 61 | 94 | 152
37 | - | 85 | 152
45 | - | 76 | 152
Maximum Steam Tracer Length between Traps - 1 inch Sch 80 pipe (CS pipe)
Length of tracers, m
kg/h steam per 100 m tracer pipe | 1 barg steam | 2.76 barg steam | 10 barg steam
7.4 | 152 | 152 | 152
14.8 | 152 | 152 | 152
22.3 | 146 | 152 | 152
30 | 128 | 152 | 152
37 | 113 | 152 | 152
45 | 100 | 152 | 152
52 | 94 | 152 | 152

## Stm Hdr Sizes for Stm Tracers
Maximum Steam Flow Rate, kg/h
Header Size, inches | Steam Pr, 1 barg | Steam Pr, 2.76 barg | Steam Pr, 10 barg
3/4 | 9 | 27 | 68
1 | 27 | 68 | 136
1.5 | 113 | 180 | 408
2 | 227 | 363 | 770
3 | 816 | 907 | 1900
4 | 907 | 1360 | 2950